METAL SOUND PROJECTOR

## CELL20/T

### Architects & Engineers Specification

The unit shall be the PENTON model CELL20/T or equal and approved. The speaker enclosure shall be constructed of high-grade extruded aluminium with a mesh grille, epoxy coated to match the enclosure. The mounting will be via a “U” shaped aluminium bracket. The speaker assembly shall comprise of 130mm dual cone loudspeaker.

A 20watt / 100 volt line, factory fitted transformer shall provide 3dB power taps.

Cable entry shall be via a single cable entry mounted on a removable rear cover and will be supplied with ceramic terminals to take 2 x 2.5mm² conductors.

The loudspeaker shall have a wide dispersion. The cone shall be high a compliance unit with a smooth extended frequency response.

### Rated power 						20w

### Tappings 100v line	20/10/5/2.5w
Effective frequency range               	110 ~16Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	88dB                                    
Dispersion at 1k/2kHz                                                 180/120
Axial Q Factor at 1k/2kHz                                    	2.6/5.9

### Colour                                                                        White

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org

METAL SOUND PROJECTOR

## CELL20/TC

### Architects & Engineers Specification

The unit shall be the PENTON model CELL20/TC or equal and approved. The speaker enclosure shall be constructed of high-grade extruded aluminium with a mesh grille, epoxy coated to match the enclosure. The mounting will be via a “U” shaped aluminium bracket. The speaker assembly shall comprise of 130mm dual cone loudspeaker.

A 20watt / 100 volt line, factory fitted transformer shall provide 3dB power taps.

Cable entry shall be via a single cable gland mounted on a removable rear cover.

The loudspeaker shall have a wide dispersion. The cone shall be high a compliance unit with a smooth extended frequency response.

The CELL20/TC will be suitable for voice alarm applications and will be supplied with ceramic terminals to take 2 x 2.5mm² conductors and a thermal fuse rated at 150˚. A 4-core fire rated cable tail should be added to ensure full compliance or the addition of a second cable entry to allow “loop in, loop out” termination.

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

### Rated power 						20w

### Tappings 100v line	20/10/5/2.5w
Effective frequency range               	110 ~16Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	88dB                                    
Dispersion at 1k/2kHz                                                 180/120
Axial Q Factor at 1k/2kHz                                    	2.6/5.9

### Colour                                                                        White

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org