### ROUND CO-AXIAL METAL
CEILING LOUDSPEAKER

RCS8/TCOAX

Architects and Engineers Specifications

This unit shall be the PENTON model RCS8/TCOAX or equal and approved. The loudspeaker baffle shall be a round two part bezel comprising an inner metal mesh grille, and chassis with integral loudspeaker having no visible fixings. Assembly shall comprise of a bass/mid-range 215mm diameter coned loudspeaker and a 25mm Mylar dome tweeter complete with 12.5mm moving coil and neodymium magnet. The unit shall be fitted with a 20 watt/100 volt line factory mounted transformer with the power taps clearly marked on the assembly.

Connection will be via a 3 way terminal capable of taking 2 x 2.5mm² conductors.

The loudspeaker shall have a wide-angle dispersion. The cone shall be a damped, high compliance type with a smooth extended frequency response.

### Rated power 	20w

### Tappings 100v line	20/10/5/2.5w
Effective frequency range              	60 ~ 20Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	91dB                                    
Dispersion at 1k/2kHz                                                 180/100
Axial Q Factor at 1k/2kHz                                    	3.0/6.5

### Colour                                                                        White RAL9016

### Ceiling Cut-out	238mm

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org

### ROUND CO-AXIAL METAL
CEILING LOUDSPEAKER

RCS8/FTSCOAX

Architects and Engineers Specifications

This unit shall be the PENTON model RCS8/FTSCOAX or equal and approved. The loudspeaker baffle shall be a round two part bezel comprising an inner metal mesh grille, and chassis with integral loudspeaker having no visible fixings. Assembly shall comprise of a bass/mid-range 215mm diameter coned loudspeaker and a 25mm Mylar dome tweeter complete with 12.5mm moving coil and neodymium magnet. The unit shall be fitted with a 20 watt/100 volt line factory mounted transformer with the power taps clearly marked on the assembly.

The loudspeaker shall have a wide-angle dispersion. The cone shall be a damped, high compliance type with a smooth extended frequency response.

The RCS8/FTSCOAX will be suitable for voice alarm applications.  In addition to the above specification will be supplied with a steel fire dome capable of withstanding 800˚C, fitted with 2 x 20mm knock-outs, 3 way ceramic terminals able to take 2 x 2.5mm² conductors and a thermal fuse rated at 150˚.

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

### Rated power 	20w

### Tappings 100v line	20/10/5/2.5w
Effective frequency range	100 ~ 20Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	94dB                                    
Dispersion at 1k/2kHz                                                 180/180
Axial Q Factor at 1k/2kHz                                    	5.5/8.6

### Colour                                                                        White RAL9016

### Ceiling Cut-out	246mm

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org