VANDALPROOF METAL CABINET LOUDSPEAKER

SENTRY6/STC

# Architects & Engineers Specification

This unit shall be the PENTON model Sentry6/STC or equal and approved. Assembly shall comprise of a 140mm diameter dual coned loudspeaker and shall be fitted with a 6watt / 100volt line factory fitted transformer.

The loudspeaker cabinet shall be constructed in cast aluminium with steel front chassis and grille all epoxy powder coated to match. Installation will be via 2 x 20 mm cable entries located at the top of the cabinet or via concealed universal mounting holes (for standard UK electrical junction boxes) at the rear. The cabinet will house ceramic termination to take 2 x 2.5mm² cables and a thermal fuse with a temperature rating of 150˚C.

This loudspeaker must be complaint to BS5839 part 8.

Transformer shall be a 100 volt line with 3 dB power taps of 6, 3, 1.5, 0.75 and 0.25watts to be clearly marked on the assembly

Loudspeaker shall have a wide-angle dispersion of 140˚@ 1 kHz. Cone shall be a damped, high compliance type with a smooth extended frequency response over a range of 200Hz ~18kHz.Sensitivity shall be a minimum of 87dB @ 1metre, 1watt test signal bandwidth 100Hz ~10kHz

All units shall be tested in accordance with BS6840 part 5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk  Web: www.penton.org