VANDALPROOF SQUARE,

FLUSH MOUNT,
 METAL CABINET LOUDSPEAKER

SENTRY6/TBBC

# Architects & Engineers Specification

This unit shall be the PENTON model SENTRYT6/TBBC or equal and approved. The assembly shall comprise of a 140mm diameter dual coned loudspeaker and shall be fitted with a 6 watt/100 volt line factory fitted transformer with the power taps clearly marked on the assembly.

The flush mount loudspeaker cabinet shall be constructed as a two-part unit to enable first and second fix installation. The back box will be manufactured in galvanised steel. Cable entry will be via 2 x 20mm cable entries located on the side and rear of the cabinet. The speaker with integrated chassis and grille will be constructed in steel and epoxy powder coated.

Loudspeaker shall have a wide-angle dispersion. The cone shall be a damped, high compliance type with a smooth extended frequency response.

The SENTRY6/TBBC will be suitable for voice alarm applications and will be supplied with ceramic terminals to take 2 x 2.5mm² conductors and a thermal fuse rated at 150˚. 

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

### Rated power 	6w

### Tappings 100v line	6/3/1.5/0.75/0.25w
Effective frequency range               	180 ~17 KHz

### SPL @ 1w/m (test signal 100Hz~10 kHz)               	92dB
Dispersion at 1 k/2kHz                                                170/120
Axial Q Factor at 1 k/2kHz                                    	2.3/4.9

### Colour                                                                        White

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org